## gen
Bus # | 1 | 2 | 3 | 4
Gen id | G | G | G | C
type | GENROU | GENROU | GENROU | GENROU
T'd0 | 8 | 8 | 8 | 8
T''d0 | 0.03 | 0.03 | 0.03 | 0.03
T'q0 | 0.4 | 0.4 | 0.4 | 0.4
T''q0 | 0.05 | 0.05 | 0.05 | 0.05
H | 6.5 | 6.5 | 6.175 | 6.175
D | 5 | 5 | 5 | 5
Xd | 1.8 | 1.8 | 1.8 | 1.8
Xq | 1.7 | 1.7 | 1.7 | 1.7
X'd | 0.3 | 0.3 | 0.3 | 0.3
X'q | 0.55 | 0.55 | 0.55 | 0.55
X''d=X''q | 0.25 | 0.25 | 0.25 | 0.25
Xl | 0.2 | 0.2 | 0.2 | 0.2
S(1.0) | 0 | 0 | 0 | 0
S(1.2) | 0 | 0 | 0 | 0
Ra | 0 | 0 | 0 | 0

## exc
Bus # | 1 | 2 | 3 | 4
Gen id | G | G | G | C
type | SEXS | SEXS | SEXS | SEXS
TA_o_TB | 0.1 | 0.1 | 0.1 | 0.1
TB | 10 | 10 | 10 | 10
K | 10 | 10 | 10 | 10
TE | 0.1 | 0.1 | 0.1 | 0.1
Emin | 0 | 0 | 0 | 0
Emax | 3 | 3 | 3 | 3

## gov
Bus # | 1 | 2 | 3 | 4
Gen id | G | G | G | C
type | TGOV1 | TGOV1 | TGOV1 | TGOV1
R | 0.33 | 0.33 | 0.33 | 0.33
T1(>0)(sec) | 2 | 2 | 2 | 2
V MAX | 1 | 1 | 1 | 1
V MIN | 0 | 0 | 0 | 0
T2(sec) | 3 | 3 | 3 | 3
T3(>0)(sec) | 15 | 15 | 15 | 15
Dt | 0.4 | 0.4 | 0.4 | 0.4

## pss
Bus #
Gen id
type
A1
A2
A3
A4
A5
A6
T1
T2
T3
T4
T5
T6
KS
LSMAX
LSMIN
VCU
VCL

## regca
Bus | 1
ID | DP
LVPL switch, 0: LVPL not present, 1: LVPL present | 1
Tg, Converter time constant, second | 0.02
Rrpwr, LVPL ramp rate limit (pu/s) | 10
Brkpt, LVPL voltage 2 (pu) | 0.9
Zerox, LVPL voltage 1 (pu) | 0.4
Lvpl1, LVPL gail (pu) | 1.22
Volim, Voltage limit for High Voltage Reactive Current Management, pu | 1.2
Lvpnt1, High Voltage point for Low Voltage Active Current Management, pu | 0.9
Lvpnt0, High Voltage point for Low Voltage Active Current Management, pu | 0.5
Iolim, Current limit for HVRCM, pu (< 0) | -1.3
Tfltr, Voltage filter time constant for LVRCM (s) | 0.02
Khv, Overvoltage compensation gain used in HVRCM (>=0 and < 1) | 0
Iqrmax, Upper limit on Rate of change for reactive curent (pu/s) | 100
Iqrmin, Lower limit on Rate of change for reactive curent (pu/s) | -100
Accel, Acc. factor for smoothing out voltage & angle calculations (>0 and <=1) | 0.7
fbase | 60
mvabase | 900

## reecb
Bus | 1
ID | DP
PFFLAG (Power factor flag): 1 - power factor control; 0: Q control | 0
VFLAG: 1 if Q control; 0 voltage control | 1
QFLAG: 1 if voltage/Q control; 0 if pf/Q control | 0
PQFLAG: 1 for P priority, 0 for Q priority | 0
Vdip (pu), low voltage threshold for reactive current injection | -99
Vup (pu), high voltage threshold for reactive current injection | 99
Trv (s), Voltage filter time constant | 0.02
dbd1 (pu), Voltage error dead band lower threshold (<=0) | 0
dbd2 (pu), Voltage error dead band upper threshold (>=0) | 0
Kqv (pu), Reactive current injection gain | 0
Iqhl (pu), Upper limit on reactive current injection Iqinj | 1.1
Iqll (pu), Lower limit on reactive current injection Iqinj | -1.1
Vref0 (pu), User defined reference (if 0, initialized by model) | 0
Tp (s), Filter time constant for electrical power | 0.05
QMax (pu), limit for reactive power regulator | 0.44
QMin (pu) limit for reactive power regulator | -0.44
VMAX (pu), Max. limit for voltage control | 1.05
VMIN (pu), Min. limit for voltage control | 0.9
Kqp (pu), Reactive power regulator proportional gain | 0
Kqi (pu), Reactive power regulator integral gain | 0.01
Kvp (pu), Voltage regulator proportional gain | 10
Kvi (pu), Voltage regulator integral gain | 60
Tiq (s), Time constant on delay s4 | 0.02
dPmax (pu/s) (>0) Power reference max. ramprate | 99
dPmin (pu/s) (<0) Power reference min. ramprate | -99
PMAX (pu), Max. power limit | 1
PMIN (pu), Min. power limit | 0
Imax (pu), Maximum allowable total converter current limit | 1.11
Tpord (s), Power filter time constant | 0.02

## repca
Bus | 1
ID | DP
Remote bus number or 0 for local voltage control | 0
Monitored branch FROM bus | 0
Monitored branch TO bus | 0
Monitored branch ID (enter within single quotes) | '0
VCFlag, droop flag (0: with droop,1: line drop compensation) | 0
RefFlag, flag for V or Q control(0: Q control, 1: V control) | 0
Fflag, 0: disable frequency control, 1: enable | 1
Tfltr, Voltage or reactive power measurement filter time constant (s) | 0.02
Kp, Reactive power PI control proportional gain (pu) | 18
Ki, Reactive power PI control integral gain (pu) | 5
Tft, Lead time constant (s) | 0
Tfv, Lag time constant (s) | 0.05
Vfrz, Voltage below which State s2 is frozen (pu) | 0
Rc, Line drop compensation resistance (pu) | 0
Xc, Line drop compensation reactance (pu) | 0
Kc, Reactive current compensation gain (pu) | 0.02
emax, upper limit on deadband output (pu) | 0.1
emin, lower limit on deadband output (pu) | -0.1
dbd1, lower threshold for reactive power control deadband (<=0) | -1
dbd2, upper threshold for reactive power control deadband (>=0) | 1
Qmax, Upper limit on output of V/Q control (pu) | 0.43
Qmin, Lower limit on output of V/Q control (pu) | -0.43
Kpg, Proportional gain for power control (pu) | 1
Kig, Proportional gain for power control (pu) | 0.05
Tp, Real power measurement filter time constant (s) | 0.25
fdbd1, Deadband for frequency control, lower threshold (<=0) | -1
fdbd2, Deadband for frequency control, upper threshold (>=0) | 1
femax, frequency error upper limit (pu) | 99
femin, frequency error lower limit (pu) | -99
Pmax, upper limit on power reference (pu) | 1
Pmin, lower limit on power reference (pu) | 0
Tg, Power Controller lag time constant (s) | 0.1
Ddn, droop for over-frequency conditions (pu) | 0
Dup, droop for under-frequency conditions (pu) | 0

## pll
Bus | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
ke | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
te | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05

## vm
Bus | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
te | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02

## mea
Bus | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Method | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## gen_para
GENROU
T'd0
T''d0
T'q0
T''q0
H
D
Xd
Xq
X'd
X'q
X''d=X''q
Xl
S(1.0)
S(1.2)
Ra

## exc_para
SEXS
TA_o_TB
TB
K
TE
Emin
Emax

## gov_para
TGOV1 | HYGOV | GAST
R | R, Permanent Droop | R(Speed Droop)
T1(>0)(sec) | r, Temporary Droop | T1(>0)
V MAX | Tr(>0) Governor Time Constant | T2(>0)
V MIN | Tf(>0) Filter Time Constant | T3(>0)
T2(sec) | Tg(>0) Servo Time Constant | Ambient Temperature Load Limit
T3(>0)(sec) | VELM, Gate Velocity Limit | KT
Dt | GMAX, Maximum Gate Limit | VMAX
| GMIN, Minimum Gate Limit | VMIN
| TW(>0) Water Time Constant | Dturb
At, Turbine Gain
Dturb, Turbine Damping
aNL, No Load Flow

## pss_para
IEEEST
A1
A2
A3
A4
A5
A6
T1
T2
T3
T4
T5
T6
KS
LSMAX
LSMIN
VCU
VCL